## Slide 1: Planning and operating for Resiliency in Water and sewer services
Bryan R. Tillery, Manager of water quality/operations
Warren county water district

## Slide 2: Warren County Water District
Joint Operations agreement with Simpson County Water District and Butler County Water System
47,000 accounts
1,200 mi2 Service area
Population served: 88,000 people

## Slide 3: Resilient system design
Storage tanks
  Distributed throughout system
  24-hour+ Average day capacity
  System pressurization via gravity

## Slide 4: Resilient system design
Flexible Piping
  Gasketed joints allow for angular deflection and axial deflection
  Axial deflection allows for thermal expansion
  Plastic material permits limited flexibility between pipe joints
  Flexible piping better accommodates ground movement

## Slide 5: Resilient system design
Redundant Facilities
  Alternative transmission routes
  Distributed transmission mains
  Looped network of pipes
Redundant components at facilities

## Slide 9: Butler County WTP Standby Power System
Challenge…
  100 year flood level at Plant’s Raw water intake is 10 feet above grade
  Plant’s raw water intake is 2,000 feet from water plant

## Slide 10: Butler County WTP Standby Power System
Solution…
  Single generator for main plant and raw water intake
  Isolate power distributor’s primary at plant
  Energize power lines to raw intake with generator
  Automatic transfer switch for plant
  Manual transfer switch for raw water intake

## Slide 11: Butler County WTP Standby Power System
Safety
  Numerous safety procedures in place
  Safety interlock disables manual switch if power line is not isolated
  manual switch door is double locked by both water district and power distributer
  Switching procedures clearly and permanently posted

## Slide 12: Resilient system Operation
Demand Response
  TVA 30 minute program
  Power Outage Exercise
“Event” Preparation
Spare & Repair components
Manual, non-automated Operability

## Slide 13: Questions…
Contact:
Bryan R. Tillery
Warren county water district
bryant@warrenwater.com
www.warrenwater.com