## Instructions
Updated May 2021
ENERGY AND ENVIRONMENT CABINET
DEPARTMENT FOR ENVIRONMENTAL PROTECTION
DIVISION OF WATER
300 SOWER BOULEVARD
FRANKFORT, KENTUCKY 40601
Instructions for Completing the Groundwater Contact-Time (C-T) Form
*This form is only applicable to systems with a treated highest pH range of 6.0-9.0.
1 | Complete the table in the Treatment Information tab. It will automatically populate the C-T form under the Virus Calculate tab.
2 | Start with your clearwell or clearwells. If you disinfect anywhere else in the treatment process, add those next. You can break the processes out to flocculation, sedimentation, and filtration.
3 | For flocculation and sedimentation, the volume will be the total volume of the basin. For filters, calculate the volume of water over the filters.
4 | The information in the C-T form in the Virus Calculate tab will be used to establish a minimum disinfectant residual unique for your water system. A 4-log removal or inactivation (disinfection) is needed for viruses to meet the Groundwater Rule. The C-T Form on the Virus Calculate tab will tell you the minimum chlorine residual needed in the clearwell to meet 4-log inactivation.
Baffling Factors (use on Treatment Information tab):
| If no baffle wall present |  | 0.1
| If one baffle wall present |  | 0.3
| If serpentine baffle wall present |  | 0.7
| If section of pipe |  | 1

## Treatment Information
ENERGY AND ENVIRONMENT CABINET
DEPARTMENT FOR ENVIRONMENTAL PROTECTION
DIVISION OF WATER
300 SOWER BOULEVARD
FRANKFORT, KENTUCKY 40601
Ground Water Rule C-T Information
Date
| Plant Name |  |  | PWS Address
| PWSID |  |  | PWS Contact
| Plant ID |  |  | PWS Phone
Treatment Process Unit |  |  | Lowest Volume | Peak Flow Rate | Baffling Factor | Disinfectant Residual | Disinfectant Type | Highest pH | Lowest Annual Water Temperature (˚C)
(Example: basin, filter, clearwell) |  |  | (gal) | (gpm) |  | (mg/L)
1
2
3 | [9 empty] | If the 'Highest pH' highlights red, this spreadsheet will not properly calculate the C-T. Please contact DOW for further assistance.
4
5
6
7
8
9
10
Pipe Volume: |  | Length (ft): |  | Diameter (in): |  | 0 | gal

## Viruses Calculate
ENERGY AND ENVIRONMENT CABINET
DEPARTMENT FOR ENVIRONMENTAL PROTECTION
DIVISION OF WATER
300 SOWER BOULEVARD
FRANKFORT, KENTUCKY 40601
Ground Water Rule C-T Calculation Form
Removal / Inactivation Requirement: Viruses
Ground Water Rule: 4-Log
DATE:
|  |  |  | Highest pH : |  | 0
PWS Name
| Plant ID: |  |  | Lowest Annual Water
| PWSID#: |  |  | Temperature (C): |  | 0
| Disinfectant |  |  | Required 4.0 Log CT Value
FALSE
| Column: |  | A | B | C | D | E | F | G | H
Unit # | Treatment Process Unit |  | Capacity | Flowrate | Detention Time (min) | Baffling Factor | Concentration of Disinfectant | Calculated C-T Value | Required 4.0-Log | C-T Ratio Achieved | Usable LOG | Required Concentration of Disinfectant to Achieve 4-LOG
|  |  | (gal) | (gpm) | =A / B |  | (mg/L) | = C x D x E | C-T Value | = F / G | (ratio achieved x 4)
1 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0 | #VALUE!
2 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
3 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
4 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
5 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
6 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
7 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
8 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
9 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
10 |  |  | C: #VALUE!; F: #VALUE!; FALSE H: #VALUE! | 0
| TOTAL |  | FALSE G: Need at least 4 logs | 0